VELTRONICS






25 Regentview Drive

Industrial Electronic Controls & Service Ltd.


Brampton, Ontario

www.veltronics.ca






L6Z 3G8  Canada


NPN/PNP Splitter

DIN rail mounted NPN/PNP Splitter was designed for industrial applications to recognize type of connected switches (proximity, limit switches, etc.) and convert PNP or NPN input signals into separated PNP and NPN outputs signals.

Block-diagram











Technical data


Power supply







+24V +/- 4V

Current consumption






max. 10 mA

Wrong polarity protection






Yes

Inactive input (open input) voltage





appx. 12V

Input impedance







10 K Ohms

Input NPN threshold






5 V

Input PNP threshold






20 V


Outputs type







open collectors

Max output current






100 mA

Max output voltage (NPN output)





40 V

Max output voltage (PNP output)





Power voltage (appx.)

Max frequency (1 K Ohm load)





100 KHz











905 840 3039 Office










905 840 2539 Fax










416 678 2834 Cell
Thresholds


scheme





+24V





Ground





PNP or NPN 





+24 V to prox.





Ground to prox.





NPN output





PNP output





Input active indicator





A





B





C





D





E





F





G





H








